OFF-GAS GAS DETECTION SYSTEM FOR LITHIUM-ION BATTERIES

- GENERAL

- The off-gas monitoring system is a system comprised off a distributed sensing network that is designed to monitor lithium-ion batteries that have vented gas. The off-gas detection system should be installed in accordance with the manufacturer’s recommendations.

- The system includes the following components:

- Sensor

- Controller

- Cable

- Adapter (optional)

- COMPONENTS

2.01 SENSORS

Monitoring Sensor, Reference Sensor

- Monitoring Sensors should be distributed in the application to monitor for lithium-ion battery cell venting.

- Reference Sensors should be distributed in the application to monitor air contaminants.

- Sensors will have power supply rated at 3 – 16 VDC.

- Sensors can communicate status of error, warm-up, normal, and alarm.

- Sensor can operate within relative humidity ranges 5 – 95% and temperature ranges of 14oF to 140oF (-10oC to 60oC). The maximum allowable temperature change is 8.6oC

- The unit will be certified to UL/IEC 61010 for product safety, EN60326-1 for EU Directive (2014/30/EU), RoHS 3 EU 2015/863 and REACH compliant.

- The sensor and controller must be manufactured in an ISO 9001:2015 production environment.

- The sensor shall be capable of self-diagnosing error states.

- The sensor should be checked with yearly maintenance checks to continue sensor performance. The validation of sensor operation shall be done in accordance with the manufacturer’s recommendations.

2.02 CONTROLLER

Monitoring & Reference Controller

- The Controller distributes power to the sensors, aggregates and processes sensor signals, and provides communication of sensor status.

- The Controller aggregates 12 Monitoring Sensors and 3 Reference Sensors

- Multiple Controllers can be used when Controllers are properly daisy chained together by c

- The Controller processes the sensor signal status and communicates if a lithium-ion battery cell venting has occurred.

- The Controller will have a power supply rated at 8 – 28 VDC.

- The Controller has a power consumption detailed in the table below:

| Detail | Specification |
| --- | --- |
| Controller (no sensors) | 2.4 W (at 24 Vdc) |
|  | 1.4 W (at 12 Vdc) |
| Sensor | 275 mW (at 5 Vdc) |
| Controller (fully populated, 15 sensors) | 6.6 W (at 24 Vdc) |
|  | 5.6 W (at 12 Vdc) |

- The Controller will be protected by a 3.5 A replaceable fuse.

- The Controller will communicate individual and aggregated sensor status’ through two digital output ports and/or MODBUS RTU RS232.

- The Controller will communicate aggregated sensor error status’ through digital output and MODBUS RTU

- The Controller will communicate individual sensor error status locally through LED indicators.

2.01 CABLES

Sensor Cable, Power Cable, Communication Cable, Daisy Chain Cable

- Monitoring Sensor Cables are black 8P8C RJ45 shielded 24-28 AWG cable.

- Reference Sensor Cables are blue 8P8C RJ45 shielded 24-28 AWG cable.

- Daisy Chain Cables are grey 8P8C RJ45 shielded 24-28 AWG cable.

- Power Cables are 3-pin Molex connectors that include earth ground and terminate in bare wire leads.

- Digital Output Cables are 10-pin Molex connectors that terminate in bare wire leads.

- Serial Cables are female-to-female RS232 cables.

2.01 ADAPTERS

MODBUS adapter, Relay

- The MODBUS TCP/IP adapter has the ability to convert the Controller’s native MODBUS RTU communication protocol to MODBUS TCP/IP.

- The Relay will turn the digital output signal into a dry contact signal.

3.00	EXECUTION

  - INSTALLATION

- The installation should be done in accordance with the manufacturer’s recommendations.

  - MAINTENANCE

- The maintenance procedure should be done in accordance with the manufacturer’s recommendations.

END OF SECTION